STATE SMALL WATER SYSTEM INSPECTION REPORT

DATE OF RE-INSPECTION: April 19, 2022

COMP#: 3303102 WA0000287

DBA: Weber Valley Heights Association

LOCATION: 44135 Perryman Lane Hemet, CA 94544

APN 571-040-004

MAILING ADDRESS: 	Jeff Hall 44350 E. Benton Road, Hemet, CA 92543

Robert Franko & Debbie St. Pierre 44135 Perryman Lane Hemet, CA 92544

OWNER\OPERATOR:  	President Jeff Hall 951-767-7072 home, 951-313-2249 cell

Robert Franko, Vice President 951-764-5081

Secretary / Treasurer Deborah St. Pierre 951-764-5059

Dan Spears, Maintenance 909-770-0852

This is a routine inspection conducted  by My Tran (Riverside County), Daisy Ciudad Real (Riverside County)  with the assistance of  Deborah St. Pierre (Secretary/Treasurer) and Robert Franko (Vice President).

TYPE OF SYSTEM

This is a State Small water system with two wells and 2 pressure zones.  There are 6 connections on each well.  There is approximately 15 permanant residents.  No future redevelopment is planned at the community.

SOURCES OF WATER AND STORAGE FACILITIES

Well No. 1 (33.592172, -116.889860)

- This Department does not have construction records.

- Well production is unknown

- Based on information provided by owner this well is 352 feet deep.  Riverside County well permit #29372 was assigned for inventory purposes only.

Well No. 2 (33.592158, -116.892457)

- This Well was constructed in December 1990, under Riverside County well permit #29371.  The well is 600 feet deep with a 50ft sanitary seal.

- The well produces approximately 9 GPM

Storage:

- This system has 3 different storage tanks.  There are two tanks for well#1 and one for well#2.

Distribution: The distribution for this system is composed of a 2” pipe that runs from well #1 through Ginger circle to Wrench Road to the two tanks at Happy Hills lane.  Same size pipe runs from well 2 to the metal tank half way up the road.

TDS was measured at 204 mg/L by conductivity and 5 psi at hose bib by metal tank.

CHEMICAL QUALITY

Arsenic, nitrate, fluoride, and the remaining inorganic chemicals were all sampled on November 1, 2013. Both well 1 and 2 results were all within acceptable standards.

| Location | Nitrate as N (µg/L) Due every year | Inorganic chemical Due every 10 years |
| --- | --- | --- |
| Well 1 | 2023 | 2023 |
| Well 2 | 2023 | 2023 |

BACTERIOLOGICAL QUALITY

Bacteriological sampling was satisfactory for the past year. Next samples are due in the 2nd quarter of 2022.

AUXILIARY SOURCES

None at this time.

BACKFLOW HAZARD

None observed at time of inspection.

EMERGENCY PROVISIONS

Water Quality Emergency Notification Plan and Bacteriological Sample Siting Plan need to be updated.

Customer yearly notification for 2022 need to be submitted.

CORRECTIONS & RECOMMENDATIONS:

Submit documents and pictures to show correction for the following by 6/30/2022

- Repair leak at check valve well#1.

- Clear vegetation around the two tanks for well#1.

- Update Water Quality Emergency Notification Plan and Bacteriological Sample Siting Plan.

- Submit yearly notification for 2022.

Please contact this Department with additional questions at 951-461-0284.

REPORT PREPARED BY:

My Tran MBA, REHS

DATE: 5/3/2022